**GTI EL5**

**GTI EL5** is a **multi-layered looselay vinyl tile**, 6 mm thick, reinforced with 2 glass fibre grids

GTI EL5 tiles can be installed using interlocking system with dove tails (**GTI EL5 CONNECT**).

They are also available in **square format with welded joints** for clean environments and watertight systems requirements (**GTI EL5 CONTROL**).

GTI EL5 wearlayer is 2 mm vinyl homogeneous manufactured with continuous high pressure process, abrasion group P.

It complies with EN 649 and offers an outstanding resistance to traffic.

This floorcovering is treated with **Evercare™** technology : the latest improvements in polyurethane surface treatment obtained by UV laser cross-linking. Evercare™ offers easy maintenance and avoids staining of chemical products used in healthcare like betadine, eosin or anti-bacterial hand gel.

This treatment has excellent maintenance characteristics; it requires no wax for life!

The carbon encapsulated granules throughout its full thickness and the **conductive backing** and **conductive surface treatment** ensure optimal and consistent conductive properties throughout its full life expectancy.

**GTI EL5** acts as a continuous conductive **5.104 ≤ Rt ≤ 106** (EN 1081)

It has permanent antistatic properties (< 20 V).

**The product is non-emissive of volatile organic compounds with <10 µg/m3 (TVOC after 28 days ISO 16000-6).**

Complementary finishes : GTI EL5 ACCESS (access ramp), GTI EL5 CORNER (corner finishes), GTI EL5 CONTROL coving (COVING / COVING CORNER IN et COVING CORNER OUT) and conductive welding rods (GTI EL5 CONTROL WELDING RODS).